Lyncean Group

68th Meeting

"Nuclear Reactor Safety and the Accident at Fukushima"

Alfred Torri

Risk Management Associates, Inc.

1421 Hymettus Avenue, Encinitas, CA.

Tel 760 436 4779. E-mail: atorri@gorma.com

December 16, 2011

Ruben H. Fleet Science Center

San Diego

# Qualifications and Experience

- Dipl. Ing. (Mechanical), ETH, Switzerland

### MS, Nuclear Engineering, MIT

### 1972			ScD, Nuclear Engineering, MIT

1967-1972		Shift Supervisor MIT Forschungsreaktor

1972-1979 	General Atomic, San Diego, Mgr. GCFR Safety and Reliability

1980-1989	Partner, Pickard, Lowe and Garrick. Level 2 PSA und Severe Accidents.

1990-1994	Independent Consultant for Safety, Reliability and Risk.

1994-Now	President, Risk Management Associates, Inc. PSA, Accident Analyses, Severe Accident Management, Severe Accident Simulators

Nuclear Power History

12/1957	Shippingport Nuclear Station, Shippingport, PA  - First commercial Nuclear Power Plat in Operation.

1957 – 1990	127 Nuclear Electric Plants (> 50 Mwe) built  in the US, 104 still in operation producing 102,391 Mwe (35 BWRs, 69 PWRs).

France	60 Nuclear Power Plants in Operation, 63,363 Mwe (59 PWRs, 1 LMFBR). One 1600 MWe under construction at Flamanville (Copy of Okiluto 3 in Finland).

China	11 Nuclear Power Plants in Operation, 8,694 Mwe (9 PWRs, 2 PHWRs). 26 under construction, 26,820 Mwe).

Worldwide	441 Nuclear Power Plants in Operation producing 374,692 Mwe, 60 Mwe under construction representing 58,584 Mwe.

Number of Nuclear Power Plants in Operation Worldwide Today

Nuclear Power Share of Electricity Today by Country

NUCLEAR POWER PLANT SAFETY

- WHY IS SAFETY SUCH A BIG ISSUE IN NUCLEAR POWER PLANTS

- WHAT ARE THE SAFETY PRINCIPALS

- DEFENSE IN DEPTH

- SAFETY BARRIERS

- PROBABILISTIC RISK ASSESSMENT

- HISTORY

- FUKUSHIMA

- SIMULATION OF AN ACCIDENT SCENARIO

WHY IS SAFETY SUCH A BIG ISSUE IN NUCLEAR POWER PLANTS

- HEAT IS PRODUCED BY FISSIONING U-235 ATOMS

- ONE FISSION RELEASES 200 MeV OF ENERGY, 97% AS KINETIC ENERGY OF THE RECOILED FISSION PRODUCT FRAGMENTS AND NEUTRONS, 3% IN THE RADIOACTIVE DECAY OF THESE FISSION PRODUCT FRAGMENTS

- FISSION PRODUCT FRAGMENTS ARE RADIOACTIVE AND DECAY OVER TIME WITH A CHARACTERISTIC HALF-LIFE RANGING FROM MILLISECONDS TO 100’s OF YEARS

- AFTER REACTOR IS SHUT DOWN (FISSION REACTION TERMINATED) RADIOACTIVE DECAY CONTINUES, RELEASING DECAY ENERGY THAT MUST BE REMOVED

- NUCLEAR FUEL MUST CONTINUE TO BE COOLED – SUBMERGED IN WASTER -  FOR ABOUT 3 YEARS AFTER SHUTDOWN

- IF FUEL BECOMES UNCOVERED IT WILL HEAT UP AND MELT, RELEASING THE GASEOUS AND VOLATILE FISSION PRODUCTS ACCUMULATED IN IT.

- FISSION PRODUCTS ARE UNSTABLE FORMS OF ELEMENTS WHICH BECOME MORE STABLE BY DECAY. DECAY EMITS RADIOACTIVE PARTICLES OR RAYS:

  - α Particle (He 2+) – Non-penetrating

  - β Particle (1- Electron) – can penetrate skin

  - γ (Energy Radiation) – deep tissue penetration

- FISSION PRODUCTS RELEASED TO THE ENVIRONMENT CAN CAUSE HEALTH EFFECTS IN PEOPLE THROUGH CLOUD EXPOSURE TO RADIATION AND TO INGESTION OF CONTAMINATED PRODUCTS:

  - 400+ REM causes death within weeks

  - 50 – 400 REM causes recoverable sickness

  - Radiation above a threshhold can cause cancer after many years

  - Level of Threshhold is not well defined and still subject to debate

  - Many natural and human caused sources of radiation: Background 0.3 to 15 REM/yr, X-ray 10 mREM, CT Scans 2 REM

  - Allowable annual radiation at a nuclear power plant:

    - Workers 5 REM/yr

    - Public – 0.1 REM/yr

WHAT ARE THE SAFETY PRINCIPALS

- Design to contain consequences of a nuclear reactor meltdown?

- 1970s Congressional rulemaking on Emergency Core Cooling Systems

  - With 1970 State of knowledge it was not considered practical to design to contain a nuclear reactor meltdown

  - Defined required redundancy in safety systems to insure low risk od a meltdown – redundant systems and single failure criterion for safety systems

  - Defined defense in depth barriers: fuel, cladding, reactor coolant system boundary, containment

- More Recently:

- ALARA – Exposure “As Low As Reasonably Achievable”

- Probabilistic Risk Assessment

- Risk vs Benefit Measures

PROBABILISTIC RISK ASSESSMENT

- WASH-1400 1975 – Rasmussen study

- What can go wrong?

- How likely is it?

- What are the consequences

- Distinguish:

  - Operation at power

  - Operation during shutdown

  - Internally caused events – anything causing a scram

  - Area events (fires, floods on-site)

  - Externally caused events (earthquakes, floods, storms, etc.)

- Level 1 PRA – What is the frequency of core damage

- Level 2 PRA - What is the frequency and magnitude of an accidental relaese

- Level 3 PRA - What is the frequency and magnitude of harm to the public

- Automation vs Operators

- Individual plant studies and NUREG-1150 (1991)

HISTORY

- Three Mile Island (TMI) - 1979:

  - Hardware malfunction and operator errors

  - Accident contained by Containment

  - No release to envirnment

  - Led to introduction of Severe Accident Management Guidelines (SAMGs)

- Chernobyl - 1986:

  - Dual purpose reactor design

    - Produce fuel for weapons

    - Produce electric power

    - No Containment

  - Operator Error in an unsafe design

    - Test after shutdown

    - Procedure required 6 hour wait time to build in Xenon poisoning

    - Conducted test without delay and caused a reactivity excursion

  - Consequences

    - Design abandoned by Russia

    - 30 plant workers and fire fighters died within weeks

    - Long term evacuation (still today) and cancer risks

    - Detectable increase in cancers above occurrence from other causes in exposed population is still debated

FUKUSHIMA

- What happened:

  - Site with 4 reactors, one was shutdown and defueled

  - Larger than design basis Earthquake failed all Electrical Power, RCIC functioned

  - 1 hour later a larger than design basis Tsunami failed battery power and RCIC

  - All core cooling lost, water boils off, core uncovers, hydrogen generation, containment pressure increase

  - Waited too long to vent containment, may have caused local containment failure

  - Waited too long to inject sea water into vessel to recover core

  - Major core melting in-vessel at 3 reactors. Some debris may have been released through reactor vessel bottom head failure into containment.

  - Containment venting released hydrogen into reactor building and caused dramatic explosions in reactor building

  - Major release of activity to environment, mostly out to sea

  - For 9 months core/debris was kept covered with water boiloff but without cooling resulting in continued low level release of activity

  - Now is core/debris actively cooled again without boiloff

  - No plant worker over-exposed (2 workers had feet over-exposed, not whole body)

  - No member of public over-exposed as far as we know

  - In long run (20 to 50 years) some additional cancer fatalities are expected

  - Probbably not detectable againnst normal variation of cancer caused deaths from all other causes

FUKUSHIMA (continued)

- Contributing Causes

  - Earthquake/Tsunami killed 25,000 people instantly

  - Inadequate response to 1996 larger than design basis earthquake at Kashiwasaki

  - No full scope risk assessments for external events

  - No or inadequate Severe Accident Management Guidelines for external events

  - No or inadequate preparation for loss of all systems

  - Inability of making unplanned decisions in an emergency

  - Decision of corrective/mitigating actions had to be made by the President of Japan

  - Larger consequences were avoided by plant manager’s unauthorized decision to turn on sea water injection and by wind predominantly out to sea

SIMULATION A SEVERE ACCIDENT

Accident Sequence Definition

- Loss of all AC power at time 0.0, recovered when water level reaches bottom of active fuel

- Loss of diesel power at time 0.0, recovered when water level reaches bottom of active fuel

- Battery power is available for 2 hours

- RCIC and HPCI fail when battery power is lost

Accident Sequence Evolution

0.0 h	Loss of power, reactor scrams, feedwater tripped

12 m 	RCIC starts automatically on low level,

16 m 	RCIC stops on high level

2.0 h 	Batteries run out and RCIC fails at 2 hours.

5.5 h	Core begins to uncover

6.0 h	Fission products begin to be released from fuel

6.5 h 	Fuel melting and relocation in core begins

7.5 h	Water level at bottom of active fuel, core slumped onto grid palte, RCIC recovered

14.7 h	RCIC supply tank runs empty, suction switched to suppression pool, temperature too high and RCIC fails due to cavitation. Core debris starts to reheat

20.5 h	Core debris melts through grid plate into lower plenum

21.0 h	Vessel lower head fails at control rod guide tube penetration, debris relocates to drywell (containment) where it is quenched by water

21.0 h	Containment pressure increases to 10.7 bar, hardened vent is opened to environment (rupture disk), gaseous and some volatile fission products and all hydrogen are vented to environment

22.8 h	Water is boiled off, debris uncovers, reheats and begins to erode into concrete. Vent remains open and activity release to environment continues at much lower level.